| Sr.No. |  |  |
| --- | --- | --- |
| 1 | Date | 16-Feb-25 |
| 2 | Structure application | Shed |
| 3 | Proposal Id | C493-012-Raipur |
| 4 | Building No. | 1 |
| 5 | Option | 1 |
| 6 | Revision | 0 |
| 7 | Area (sqm) | 4875 |
| 8 | Design Software | MBS |
| Sr.No. | Parameter | Details |
| 1 | Building type | Clear Span |
| 2 | Length in m (o/o of steel) | Ref fig |
| 3 | Width in m (o/o of steel) | Ref fig |
| 4 | Left clear height in m | 10.7 |
| 5 | Right clear height in m | 10.7 |
| 6 | Ridge line distance | Ref fig |
| 7 | Roof slope (?:100) | 10/100 |
| 8 | Left end wall bay spacing in m | Ref fig |
| 9 | Right end wall bay spacing in m | Ref fig |
| 10 | Side wall bay spacing | Ref fig |
| 11 | Wall bracing type | Rod |
| 12 | Roof bracing type | Rod |
| 13 | Roof sheeting | 0.45mm aluzinc |
| 14 | Wall sheeting | 0.45mm aluzinc |
| 15 | Doors | Ref fig |
| 16 | Windows | NA |
| 17 | Block wall in m | 3.6 |
| 18 | Rigid frames interior column locations | 2@15 |
| Sr no. | Item | Details |
| 1 | Canopy Extension in m | NA |
| 2 | Slope | 10/100 |
| 3 | Clear top height in m | NA |
| Sr no. | Accessories |  |
| 1 | Braced bays (Bay id) | Ref fig |
| 2 | Skylights (FRP 3.25m x 1m) | NA |
| 3 | Turbo Ventilators (600 mm throat diameter) | NA |
| 4 | Base Elevation | NA |
| 5 | Bay Id @ Left end wall | NA |
| 6 | Bay Id @ Front side wall | NA |
| 7 | Bay Id @ Right end wall | NA |
| 8 | Bay Id @ Back side wall | NA |

| Sr no. | Parameter | Details |
| --- | --- | --- |
| 1 | Desing code | AISC code |
| 1 | Dead Load in kN/m2 | 0.1 |
| 2 | Live Load in kN/m2 | 0.57 |
| 3 | Collateral load kN/m2 | 0 |
| 4 | Max wind speed in m/s | 47 |
| 5 | Max rainfall intensity in mm/hr | 150 |
| 6 | Exposure category | B |
| 7 | Seismic zone co-efficient (III) | 0.16 |
| 8 | Maximum temperate variation | 20 |
| Sr no. | Parameter | Details |
| 1 | Frames Vertical deflection | Span/150 |
| 2 | Frames Horizontal deflection | Height/100 |
| 3 | Purlins | Span/150 |
| 4 | Girts | Span/120 |
| 5 | Crane beams | Span/600 |
| 6 | Mezzanine beams | Span/240 |
| 7 | Misc |  |
| Sr no. | Assumption/Remark | Details |
| 1 | Hot rolled sections grade (Mpa) | 250 |
| 2 | Cold form sections grade (Mpa) | 350 |
| 3 | Primary sections grade (Mpa) | 350 |
| 4 | Building design condition | Enclosed |
| 4 | Minimum web thickness in mm | 4 |
| 5 | Minimum flange thickness in mm | 5 |
| 6 | Minimum flange width in mm | 150 |
| 7 | Minimum web depth in mm | 250 |
| 8 | Minimum cold form thickness in mm | 1.5 |
| 9 | Sheeting profile width & length in m | 1.22 & 7.65 |
| 10 | Connection bolts grade | High strength bolts (ASTM A325 or equivalent) |

| Sr no. | Parameter | Details |
| --- | --- | --- |
| 1 | Crane Capacity in kN | 1000 |
| 2 | Crane bracket height in m | 7.62 |
| 3 | Crane span in m | 13.3 +/- |
| 4 | Crane running length in m | 75 |
| 5 | Crane class | II (Normal duty) |
| 6 | Crane Type | Top running |
| 7 | Type of Girder | Double |
| 8 | Bridge Weight in MT | 56 |
| 9 | Hoist/Trolley Weight in MT | 21.5 |
| 10 | Number of Wheels | 8 |
| 11 | Wheel Load in MT | 30.5 |
| 12 | Wheel Base in mm | 4500 |

| Sr no. | Parameter | Details |
| --- | --- | --- |
| 1 | Crane Capacity in kN | 350 |
| 2 | Crane bracket height in m | 7.65 |
| 3 | Crane span in m | 13.3 +/- |
| 4 | Crane running length in m | 75 |
| 5 | Crane class | II (Normal duty) |
| 6 | Crane Type | Top running |
| 7 | Type of Girder | Double |
| 8 | Bridge Weight in MT | 23 |
| 9 | Hoist/Trolley Weight in MT | 6.5 |
| 10 | Number of Wheels | 4 |
| 11 | Wheel Load in MT | 22.5 |
| 12 | Wheel Base in mm | 3800 |

| Sr no. | Parameter | Details |
| --- | --- | --- |
| 1 | Crane Capacity in kN | 100 |
| 2 | Crane bracket height in m | 7.62 |
| 3 | Crane span in m | 13.3 +/- |
| 4 | Crane running length in m | 75 |
| 5 | Crane class | II (Normal duty) |
| 6 | Crane Type | Top running |
| 7 | Type of Girder | Double |
| 8 | Bridge Weight in MT | 23 |
| 9 | Hoist/Trolley Weight in MT | 4.5 |
| 10 | Number of Wheels | 4 |
| 11 | Wheel Load in MT | 11.5 |
| 12 | Wheel Base in mm | 3500 |

| Sr no. | Parameter | Details |
| --- | --- | --- |
| 1 | Crane Capacity in kN | 50 |
| 2 | Crane bracket height in m | 7.62 |
| 3 | Crane span in m | 13.3 +/- |
| 4 | Crane running length in m | 75 |
| 5 | Crane class | II (Normal duty) |
| 6 | Crane Type | Top running |
| 7 | Type of Girder | Double |
| 8 | Bridge Weight in MT | 17.5 |
| 9 | Hoist/Trolley Weight in MT | 3 |
| 10 | Number of Wheels | 4 |
| 11 | Wheel Load in MT | 7.2 |
| 12 | Wheel Base in mm | 3200 |