## WIND LOAD CALCULATION
WIND LOAD CALCULATION SHEET
LENGTH (L) | = | 100 | m | Basic Wind speed,Vb= | 47 | m/s
WIDTH(W) | = | 15 | m | Terrian Category = | 2
HEIGHT(H) | = | 11.2 | m | Bay Spacing(sidewall) = | 7.5 | End = | 7.5
SLOPE = | 1 | 10 |  | Enclosed Condition | 0.2 | -0.2
Calculation for wind pressure : | [8 empty] | Terrian Category
k1 = | 1 | General building, As per Table-1 of IS-875-Part-3 | [5 empty] | Height | 1 | 2 | 3 | 4
k2 = | 1.02 | For Terrian category 2 as per Table 2, Clause: 6.3.2.1-b | [5 empty] | 10 | 1.05 | 1 | 0.91 | 0.8
k3 = | 1 | Upwind slope is less than 3 degree | [5 empty] | 15 | 1.09 | 1.05 | 0.97 | 0.8
k4 = | 1 | for Non Cyclonic Region | [5 empty] | 20 | 1.12 | 1.07 | 1.01 | 0.8
Vz = | k1xk2xK3xK4XVb = |  |  | 47.94 m/s |  |  |  | 30 | 1.15 | 1.12 | 1.06 | 0.97
wind pressure Pz = 0.6Vz^2 = |  |  |  | 1378.95 N/m2 = | 1.3789 | kN/m2 |  | 50 | 1.2 | 1.17 | 1.12 | 1.1
Kd = | 0.9 | (Directionality factor) | [5 empty] | 11.2 | 1.0596 | 1.012 | 0.9244 | 0.8
Ka = | 0.8 | (Area Averaging factor)
Kc = | 0.9 | (Combination factor for pressure & Suction)
Design wind pressure Pd(not be taken less than 0.7Pz) KdxKaxKcxPz = |  |  |  | 0.9 | kN/m2
H/W = | 0.74667 | 0.5<h/w≤1.5
L/W = | 6.6667 | l/w>4
h/w≤0.5
0.5<h/w≤1.5
Wind load on frame
CASE-1- WIND ACROSS THE RIDGE(ZERO DEGREE) Positive Cpi | [11 empty] | 1.5<h/w<6
SURFACE | Cpe | Cpi | Cp=(Cpe-Cpi) | Wind load on frame
A | 0.7 | 0.2 | 0.5 | 0.5x0.9x7.5= | 3.375
EF | -0.9 | 0.2 | -1.1 | -1.1x0.9x7.5= | -7.425 | [6 empty] | 1<l/w≤1.5
GH | -0.6 | 0.2 | -0.8 | -0.8x0.9x7.5= | -5.4 | [6 empty] | 1.5<l/w≤4
B | -0.3 | 0.2 | -0.5 | -0.5x0.9x7.5= | -3.375 | [6 empty] | l/w>4
C | -0.7 | 0.2 | -0.9 | -0.9x0.9x7.5= | -6.075
D | -0.7 | 0.2 | -0.9 | -0.9x0.9x7.5= | -6.075
CASE-2- WIND ACROSS THE RIDGE(ZERO DEGREE) Negative Cpi
SURFACE | Cpe | Cpi | Cpe-Cpi | Wind load on frame
A | 0.7 | -0.2 | 0.9 | 0.9x0.9x7.5= | 6.075
EF | -0.9 | -0.2 | -0.7 | -0.7x0.9x7.5= | -4.725
GH | -0.6 | -0.2 | -0.4 | -0.4x0.9x7.5= | -2.7
B | -0.3 | -0.2 | -0.1 | -0.1x0.9x7.5= | -0.675 |  |  | TRANSVERSE WIND |  |  |  |  | LONGITUDINAL WIND
C | -0.7 | -0.2 | -0.5 | -0.5x0.9x7.5= | -3.375
D | -0.7 | -0.2 | -0.5 | -0.5x0.9x7.5= | -3.375 |  |  | Height | Length |  |  |  | Height | Length
CASE-3- WIND PARALLEL TO RIDGE(90 DEGREE) WITH Posative Cpi | [9 empty] | Windward |  |  |  |  | Windward
SURFACE | Cpe | Cpi | Cpe-Cpi | Wind load on frame |  |  |  | h/w≤0.5 | 1<l/w≤1.5 | 0.7 | -0.5 |  | h/w≤0.5 | 1<l/w≤1.5 | -0.5
A | -0.5 | 0.2 | -0.7 | -0.7x0.9x7.5= | -4.725 |  |  |  | 1.5<l/w≤4 | 0.7 | -0.6 |  |  | 1.5<l/w≤4 | -0.5
EG | -0.9 | 0.2 | -1.1 | -1.1x0.9x7.5= | -7.425 |  |  |  | l/w>4 | 0.7 | -0.6 |  |  | l/w>4 | -0.5
EG | -0.6 | 0.2 | -0.8 | -0.8x0.9x7.5= | -5.4 |  |  | 0.5<h/w≤1.5 | 1<l/w≤1.5 | 0.7 | -0.5 |  | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.6
B | -0.5 | 0.2 | -0.7 | -0.7x0.9x7.5= | -4.725 |  |  |  | 1.5<l/w≤4 | 0.7 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
C | 0.7 | 0.2 | 0.5 | 0.5x0.9x7.5= | 3.375 |  |  |  | l/w>4 | 0.7 | -0.7 |  |  | l/w>4 | -0.5
D | -0.1 | 0.2 | -0.3 | -0.3x0.9x7.5= | -2.025 |  |  | 1.5<h/w<6 | 1<l/w≤1.5 | 0.8 | -0.8 |  | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
CASE-4- WIND PARALLEL TO RIDGE(90 DEGREE) WITH Negative Cpi | [8 empty] | 1.5<l/w≤4 | 0.7 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
SURFACE | Cpe | Cpi | Cpe-Cpi | Wind load on frame |  |  |  |  | l/w>4 | 0.7 | -0.7 |  |  | l/w>4 | -0.5
A | -0.5 | -0.2 | -0.3 | -0.3x0.9x7.5= | -2.025
EG | -0.9 | -0.2 | -0.7 | -0.7x0.9x7.5= | -4.725
EG | -0.6 | -0.2 | -0.4 | -0.4x0.9x7.5= | -2.7 |  |  | Height | Length |  |  |  | Height | Length
B | -0.5 | -0.2 | -0.3 | -0.3x0.9x7.5= | -2.025 |  |  |  |  | Leeward |  |  |  |  | Leeward
C | 0.7 | -0.2 | 0.9 | 0.9x0.9x7.5= | 6.075 |  |  | h/w≤0.5 | 1<l/w≤1.5 | -0.2 | -0.5 |  | h/w≤0.5 | 1<l/w≤1.5 | -0.5
D | -0.1 | -0.2 | 0.1 | 0.1x0.9x7.5= | 0.675 |  |  |  | 1.5<l/w≤4 | -0.25 | -0.6 |  |  | 1.5<l/w≤4 | -0.5
[9 empty] | l/w>4 | -0.25 | -0.6 |  |  | l/w>4 | -0.5
[8 empty] | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.25 | -0.6 |  | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.6
[9 empty] | 1.5<l/w≤4 | -0.3 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
[9 empty] | l/w>4 | -0.3 | -0.7 |  |  | l/w>4 | -0.5
[8 empty] | 1.5<h/w<6 | 1<l/w≤1.5 | -0.25 | -0.8 |  | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
[9 empty] | 1.5<l/w≤4 | -0.4 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
[9 empty] | l/w>4 | -0.4 | -0.7 |  |  | l/w>4 | -0.5
[8 empty] | h/w≤0.5 | 1<l/w≤1.5 | -0.5
[9 empty] | 1.5<l/w≤4 | -0.6
[9 empty] | l/w>4 | -0.6
[8 empty] | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.5
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7
[8 empty] | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7
[8 empty] | Height | Length
[8 empty] | h/w≤0.5 | 1<l/w≤1.5 | -0.5
[9 empty] | 1.5<l/w≤4 | -0.6
[9 empty] | l/w>4 | -0.6
[8 empty] | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.6
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7
[8 empty] | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7