## PEB Specifications
Sr.No. | Date | 8 May 2023 | Sr no. | Parameter | Details
1 | Client | Sivoko | 1 | Desing code | MBMA
2 | Project Location | Ghana | 1 | Dead Load in kN/m2 | 0.10
3 | Proposal Id | Q-1247 | 2 | Live Load in kN/m2 | 0.575
4 | Project | Pharma | 3 | Collateral load kN/m2 | 0.05
5 | Building No. | 1 | 4 | Max wind speed in m/s | 39
6 | Option | 7 | 5 | Max rainfall intensity in mm/hr | 150
7 | Revision | 0 | 6 | Exposure category | B
8 | Structure application |  | 7 | Seismic zone | II (0.1)
8 | Design software |  | 8 | Maximum temperate variation | 20 degrees
Sr.No. | Parameter | Details | Sr no. | Parameter | Details
1 | Building type | Multi span | 1 | Frames | H/100, L/150
2 | Length in m (o/o of steel) |  | 2 | Purlins | Span/150
3 | Width in m (o/o of steel) |  | 3 | Girts | Span/120
4 | Clear height in m |  | 4 | Crane beams | Span/600
5 | Roof slope (?:100) | Slope: 10:100 | 5 | Mezzanine beams | Span/240
6 | Left end wall bay spacing in m |  | 6 | Misc
7 | Right end wall bay spacing in m |  | Sr no. | Assumption/Remark | Details
8 | Side wall bay spacing |  | 1 | Hot rolled sections grade (Mpa) | 250
9 | Wall bracing type |  | 2 | Cold form sections grade (Mpa) | 345
10 | Roof bracing type |  | 3 | Primary sections grade (Mpa) | 345
11 | Roof sheeting | 0.45 mm Aluzinc coated steel panels | 4 | Building design condition | Closed
12 | Wall sheeting | 0.45 mm Aluzinc coated steel panels | 4 | Minimum web thickness in mm | 4
13 | Doors |  | 5 | Minimum flange thickness in mm | 5
14 | Windows |  | 6 | Minimum flange width in mm | 125
15 | Block wall |  | 7 | Minimum web depth in mm | 250
Sr no. | Item | Details | 8 | Minimum cold form thickness in mm | 1.5
1 | Canopy Extension in m | 1.5 | 9 | Sheeting profile width & length in m | 1.22 & 9
2 | Slope | 1:10 | 10 | Connection bolts grade | high strength machine bolts( ASTM A325 or equivalent)
3 | Clear height in m | 0.5m above the openings
Sr no. | Accessories
1 | Wall Lights (FRP 3.25m x 1m) | Nos.
2 | Skylights (FRP 3.25m x 1m) | Nos.
3 | Turbo Ventilators (600 mm throat diameter) | Nos.

## Crane & mezzanine
Sr no. | Parameter | Details
1 | Crane Capacity in MT
2 | Crane beam top height in m
3 | Crane span in m
4 | Crane running length in m
5 | Crane class | II (Normal duty)
6 | Crane Type | Top running
7 | Type of Girder | Single
10 | Bridge Weight in MT
11 | Hoist/Trolley Weight in MT
12 | Number of Wheels | 2
13 | Wheel Load in MT
14 | Wheel Base in mm
Sr no. | Parameter | Details
1 | Location
2 | Loading
| Live load in kN/m2 | 5
| Dead load in kN/m2 | 2.5
| Collateral load in kN/m2 | 0
3 | Dimensions | -
Length in m
Width in m
Top of the Mezzanine Floor in m
| Depth of mezzanine slab in mm | 100
| Deck sheeting thickness | 0.7 mm
4 | Accessories
| Staircase Nos. | 1
| Type | Double staircase with intermediate landing
| Handrail (1m height ) | on the open side of mezzanine

## Extras
Sr no. | Items | Details
1 | Cable tray brackets | bracket lenth
4 | Walkway details | Length in m: Width in m: Height in m: Loading:
7 | Jack beam | location
8 | Parttion wall | Length in m: Width in m: Height in m: Location:
11 | Roof Insulation
12 | Wall Insulation
13 | Monkey laader | location
14 | Fascia | Length in m: Width in m: Height in m:
16 | Gable extension in m
17 | Eave extension in m
18 | Roof Monitor | Length in m: Width in m: Height in m:
19 | Cage ladder | NA
20 | Ridge Ventilators | NA
21 | Any other | NA