## WIND LOAD CALCULATION
WIND LOAD CALCULATION SHEET
LENGTH (L) | = | 126 | m | Basic Wind speed,Vb= | 39 | m/s
WIDTH(W) | = | 41.5 | m | Terrian Category = | 2
HEIGHT(H) | = | 7 | m | Bay Spacing(sidewall) = | 7.2 | End = | 7
SLOPE = | 1 | 20 |  | Enclosed Condition | 0.5 | -0.5
Calculation for wind pressure : | [8 empty] | Terrian Category
k1 = | 1 | General building, As per Table-1 of IS-875-Part-3 | [5 empty] | Height | 1 | 2 | 3 | 4
k2 = | 1 | For Terrian category 2 as per Table 2, Clause: 6.3.2.1-b | [5 empty] | 10 | 1.05 | 1 | 0.91 | 0.8
k3 = | 1 | Upwind slope is less than 3 degree | [5 empty] | 15 | 1.09 | 1.05 | 0.97 | 0.8
k4 = | 1 | for Non Cyclonic Region | [5 empty] | 20 | 1.12 | 1.07 | 1.01 | 0.8
Vz = | k1xk2xK3xK4XVb = |  |  | 39 m/s |  |  |  | 30 | 1.15 | 1.12 | 1.06 | 0.97
wind pressure Pz = 0.6Vz^2 = |  |  |  | 912.6 N/m2 = | 0.9126 | kN/m2 |  | 50 | 1.2 | 1.17 | 1.12 | 1.1
Kd = | 0.9 | (Directionality factor) | [5 empty] | 7 | 1.05 | 1 | 0.91 | 0.8
Ka = | 0.9 | (Area Averaging factor)
Kc = | 0.9 | (Combination factor for pressure & Suction)
Design wind pressure Pd(not be taken less than 0.7Pz) KdxKaxKcxPz = |  |  |  | 0.67 | kN/m2
H/W = | 0.16867 | h/w≤0.5
L/W = | 3.0361 | 1.5<l/w≤4
h/w≤0.5
0.5<h/w≤1.5
Wind load on frame
CASE-1- WIND ACROSS THE RIDGE(ZERO DEGREE) Positive Cpi | [11 empty] | 1.5<h/w<6
SURFACE | Cpe | Cpi | Cp=(Cpe-Cpi) | Wind load on frame
A | 0.7 | 0.5 | 0.2 | 0.2x0.67x7.2= | 0.9648
H | -1 | 0.5 | -1.5 | -1.5x0.67x7.2= | -7.236 | [6 empty] | 1<l/w≤1.5
L | -0.5 | 0.5 | -1 | -1x0.67x7.2= | -4.824 | [6 empty] | 1.5<l/w≤4
B | -0.25 | 0.5 | -0.75 | -0.75x0.67x7.2= | -3.618 | [6 empty] | l/w>4
C | -0.6 | 0.5 | -1.1 | -1.1x0.67x7= | -5.159
D | -0.6 | 0.5 | -1.1 | -1.1x0.67x7= | -5.159
CASE-2- WIND ACROSS THE RIDGE(ZERO DEGREE) Negative Cpi
SURFACE | Cpe | Cpi | Cpe-Cpi | Wind load on frame
A | 0.7 | -0.5 | 1.2 | 1.2x0.67x7.2= | 5.7888
H | -1 | -0.5 | -0.5 | -0.5x0.67x7.2= | -2.412
L | -0.5 | -0.5 | 0 | 0x0.67x7.2= | 0
B | -0.25 | -0.5 | 0.25 | 0.25x0.67x7.2= | 1.206 |  |  | TRANSVERSE WIND |  |  |  |  | LONGITUDINAL WIND
C | -0.6 | -0.5 | -0.1 | -0.1x0.67x7= | -0.469
D | -0.6 | -0.5 | -0.1 | -0.1x0.67x7= | -0.469 |  |  | Height | Length |  |  |  | Height | Length
CASE-3- WIND PARALLEL TO RIDGE(90 DEGREE) WITH Posative Cpi | [9 empty] | Windward |  |  |  |  | Windward
SURFACE | Cpe | Cpi | Cpe-Cpi | Wind load on frame |  |  |  | h/w≤0.5 | 1<l/w≤1.5 | 0.7 | -0.5 |  | h/w≤0.5 | 1<l/w≤1.5 | -0.5
A | -0.5 | 0.5 | -1 | -1x0.67x7.2= | -4.824 |  |  |  | 1.5<l/w≤4 | 0.7 | -0.6 |  |  | 1.5<l/w≤4 | -0.5
H | -1 | 0.5 | -1.5 | -1.5x0.67x7.2= | -7.236 |  |  |  | l/w>4 | 0.7 | -0.6 |  |  | l/w>4 | -0.5
L | -1 | 0.5 | -1.5 | -1.5x0.67x7.2= | -7.236 |  |  | 0.5<h/w≤1.5 | 1<l/w≤1.5 | 0.7 | -0.5 |  | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.6
B | -0.5 | 0.5 | -1 | -1x0.67x7.2= | -4.824 |  |  |  | 1.5<l/w≤4 | 0.7 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
C | 0.7 | 0.5 | 0.2 | 0.2x0.67x7= | 0.938 |  |  |  | l/w>4 | 0.7 | -0.7 |  |  | l/w>4 | -0.5
D | -0.1 | 0.5 | -0.6 | -0.6x0.67x7= | -2.814 |  |  | 1.5<h/w<6 | 1<l/w≤1.5 | 0.8 | -0.8 |  | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
CASE-4- WIND PARALLEL TO RIDGE(90 DEGREE) WITH Negative Cpi | [8 empty] | 1.5<l/w≤4 | 0.7 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
SURFACE | Cpe | Cpi | Cpe-Cpi | Wind load on frame |  |  |  |  | l/w>4 | 0.7 | -0.7 |  |  | l/w>4 | -0.5
A | -0.5 | -0.5 | 0 | 0x0.67x7.2= | 0
H | -0.5 | -0.5 | 0 | 0x0.67x7.2= | 0
L | -0.5 | -0.5 | 0 | 0x0.67x7.2= | 0 |  |  | Height | Length |  |  |  | Height | Length
B | -0.5 | -0.5 | 0 | 0x0.67x7.2= | 0 |  |  |  |  | Leeward |  |  |  |  | Leeward
C | 0.7 | -0.5 | 1.2 | 1.2x0.67x7= | 5.628 |  |  | h/w≤0.5 | 1<l/w≤1.5 | -0.2 | -0.5 |  | h/w≤0.5 | 1<l/w≤1.5 | -0.5
D | -0.1 | -0.5 | 0.4 | 0.4x0.67x7= | 1.876 |  |  |  | 1.5<l/w≤4 | -0.25 | -0.6 |  |  | 1.5<l/w≤4 | -0.5
[9 empty] | l/w>4 | -0.25 | -0.6 |  |  | l/w>4 | -0.5
[8 empty] | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.25 | -0.6 |  | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.6
[9 empty] | 1.5<l/w≤4 | -0.3 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
[9 empty] | l/w>4 | -0.3 | -0.7 |  |  | l/w>4 | -0.5
[8 empty] | 1.5<h/w<6 | 1<l/w≤1.5 | -0.25 | -0.8 |  | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
[9 empty] | 1.5<l/w≤4 | -0.4 | -0.7 |  |  | 1.5<l/w≤4 | -0.5
[9 empty] | l/w>4 | -0.4 | -0.7 |  |  | l/w>4 | -0.5
[8 empty] | h/w≤0.5 | 1<l/w≤1.5 | -0.5
[9 empty] | 1.5<l/w≤4 | -0.6
[9 empty] | l/w>4 | -0.6
[8 empty] | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.5
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7
[8 empty] | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7
[8 empty] | Height | Length
[8 empty] | h/w≤0.5 | 1<l/w≤1.5 | -0.5
[9 empty] | 1.5<l/w≤4 | -0.6
[9 empty] | l/w>4 | -0.6
[8 empty] | 0.5<h/w≤1.5 | 1<l/w≤1.5 | -0.6
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7
[8 empty] | 1.5<h/w<6 | 1<l/w≤1.5 | -0.8
[9 empty] | 1.5<l/w≤4 | -0.7
[9 empty] | l/w>4 | -0.7